# Purpose

This procedure describes the method of sampling for the Purified Water (PW) system within Building 902 Pilot Plant and the review and trending of the purified water test results to confirm that the quality of water produced by this GMP system can be reliably assessed.

# Scope

This procedure applies to the routine sampling and the results review for the PW system within the Pilot Plant at Sandwich. Sampling and results review for the PW system is routinely performed by the B902 Operational Team.

Testing of water samples is conducted by a contract facility.

# Safety

Risk Assessment ASYM/TB/0000030 applies to this procedure. The main risks to personnel are associated with:

  - Use of Isopropanol on sampling points. Use gloves and glasses as PPE.

  - Slips due to water spillage and trips due to low level pipework and framework.

  - Use of suitable long sleeve clothing to avoid skin contact with hot pipework.

# Apparatus Required for Sampling

4.1	The following consumables are used during the water sampling operation:

    - Sterile plastic bottles containing Sodium Thiosulphate (120mg/litre) (dosed)

    - Sterile plastic bottles, plain (undosed)

    - Disposable nitrile gloves (or equivalent)

    - 70% Isopropyl Alcohol (IPA) spray

    - Nalgene bottles (for endotoxin analysis)

    - Certified (<10 ppb) TOC Vials (Only if off-line TOC analysis is required).

    - Graduated container for the pre flushing of the purified water meter and hoses

4.2	Store all samples bottles in clean, dry environment, appropriately protected from dust or chemical contamination. Bottles found with damaged or broken seals must not be used.

4.3	Use clean gloves and wear PPE for the handling of the IPA spray, and whilst sampling.

# Sample Labelling

5.1 	Prior to sampling, determine from the schedule (QF13070) what sample points require sampling and the analysis requirements, label the required sample bottles (as specified in Table 1) using an indelible marker, with the following information:

    - Asymchem Building number and sample point reference

    - Date

    - Sampler’s initials

Note:

On Endotoxin and Chemical bottles, the time is also added. Do not use sample bottles if damaged or if the seal is not intact.

5.2	Once sampled, record the approximate time of sampling on the sample bottles collected for chemical and microbial analysis.

Table 1: Sample Requirements

| Testing Requirements | Bottle Type | Minimum Sample Volume |
| --- | --- | --- |
| TOC | Certified (<10 ppb) TOC Vials a | 2 x 40ml for TOC analysis |
| Microbial count and absence of Coliforms | Sterilin b | 500ml for all sample points |

a not required for routine testing, only used if off-line TOC analysis is required due to problems with the equipment used for on-line analysis.

b dosed for mains and softened samples (with Sodium Thiosulphate by the manufacturer), undosed for other sample types.

# General Sampling Requirements

6.1	Sampling is performed by the appropriately trained personnel in accordance with the sampling schedule.

6.2	Asymchem in Building 530 may source PW from the Pilot Plant by using a new clean container, filling from a user point and labelling as PW with time / date, initials. The PW sourced in this way is discarded after 24 hours if intended for API final step or 48 hours for any other use.

6.3	Where there is no drain, place a suitable waste container under the sample valve / user point to collect the discharge water. If it’s not possible to collect the discharged water e.g. sample valves on the PW Generation Skid, flush onto the plant room floor, ensuring that the water is cleared up when sampling is completed.

6.4	Wear a pair of disposable nitrile gloves during sampling, change gloves for each sample area and spray with 70% IPA with two minutes contact / drying time prior to sampling. If there is more than one sample required in an area spray the gloves with 70% IPA between samples, again allowing two minutes contact / drying time prior to sampling.

6.5	Sampling is performed from best water quality to worst i.e., from user points, SP12, SP09, CEDI-V103 to SP06.

6.6	Ensure sample valves / user points are opened sufficiently to ensure full flushing of the point i.e., the flush should have a substantial flow but avoid “splash-back” onto the sample valve / user point from adjacent surfaces.

6.7	Avoid contact between the inner surfaces of the sample bottle or lid and the sample valve / user point or sampler, sample by tilting the container at an angle.

6.8	If the PW complies with the requirement for Conductivity prescribed for PW in bulk, it is not necessary to carry out the test for Heavy Metals.

6.9	Additional samples may be taken for endotoxin analysis where PW is used for the final isolation and purification of API intended for use in a sterile, non- parenteral or parenteral drug product. This will be project specific based on consultation with the project team.

6.10	Analysis for Conductivity and TOC on the PW distribution loop is routinely performed on-line. If problems are encountered with the equipment used for on-line analysis of Conductivity and TOC or on-line Conductivity results exceed the United States Pharmacopeia (USP) Stage 1 specification, samples will be taken for off-line analysis.

6.11	When sampling from the PW Generation Skid, check the plant room control panel prior to sampling to confirm the system is operating normally. If the softener ‘REGEN’ light is illuminated, do not sample until the regeneration process is completed.

6.12	Sampling is undertaken weekly in accordance with the schedule (QF13070). Sampling may be performed on an alternative day or sampling taken at other points on the system if agreed by the Operations and Facility Lead. If a scheduled sample cannot be collected e.g., due to manufacturing activities, ensure that the missed sample is taken at the earliest available opportunity.

6.13	During Pilot Plant shutdowns e.g., Christmas and planned / unplanned engineering shutdowns, sampling may be suspended for the duration of the shutdown in agreement with the Operations and Facility Lead, as manufacturing activities will have been suspended. Where appropriate the PW system will remain operational during these shutdowns and will continue to be monitored by the Process Control System (PCS).

# Sampling for Microbial and Endotoxin Analysis

7.1	With the sample valve closed, spray the sample valve with 70% IPA ensuring thorough coverage both inside and outside of the chamber, allow a minimum of two minutes contact time prior to sampling for microbial or endotoxin analysis. If endotoxin and microbial sampling at the user points is required, IPA spray is not required.

7.2	Open the sample valve / user point and flush for at least one minute.

7.3	Once flushing has been completed, reduce the flow to avoid “splash-back” and collect the sample ensuring an air gap of approximately 3 cm remains in the bottle for microbial analysis and approximately 1 cm remains in the bottle for endotoxin analysis.

7.4	Use sterile bottles containing Sodium Thiosulphate for Mains and Softened water samples, an undosed bottle for partially PW and PW and a Nalgene bottle for endotoxin samples.

7.5	After sampling replace the bottle lid, close the sample valve.

7.6	Spray the sample valve with 70% IPA ensuring thorough coverage both inside and outside of the chamber.

# Receipt and Review of PW Test Results

8.1	PW test results are received from the contract sample test lab.  The results are reviewed and compared to the in-house alert and action limits (Table 3) within 48 hours of receipt.

Table 2 : TVC In–house alert and action limits

| Sample Point Reference | Water Type | Point in water system | Alert Limit (cfu/100mL) | Action Limit (cfu/100mL) | Pseudomonas Aeruginosa |
| --- | --- | --- | --- | --- | --- |
| SP06 | Softened | Pre-treated | FIO | FIO | N/A |
| V103 | Partially purified | Generation skid | 30 | 50 | N/A |
| SP09 | Partially purified | Post UV, generation skid | 5 | 10 | N/A |
| SP12 | Purified water | Storage and distribution | 5 | 10 | Presence |
| User Points | Purified water | Distribution | 5 | 10 | Presence |

FIO = For information only

Cfu = Colony forming units

Table 3: Endotoxin limit

| Endotoxin | 0.25 EU / mL |
| --- | --- |

Review the contract lab final report to confirm the following:

- Header information is correct including but not limited to:

  - Dates

  - Sample point reference

  - Company name

- The report is approved by the contract laboratory

- Any contract laboratory deviation listed must be considered for potential water quality impact.  Seek guidance from Operations and Facility Lead and / or QA if required.

- The TVC results meet or are equal to the in-house action and alert limits in Table 2.

8.2	If results exceed the figures for TVC in Table 2 the following actions must be taken

- If any result exceeds an in-house action limit in Table 2, notify the Operations and Facility Lead and Asymchem Quality Assurance (QA) Team for impact assessment and a deviation raised per SOP-QAC-002 Deviation Investigation, Asymchem Sandwich.

- For distribution system samples that exceed the in-house alert limit on two weeks consecutively or two samples in a single week, the reviewer will notify QA and take actions as decided between the users, Facilities/Operations Team and QA.

- Actions taken in response to limit excursions must be documented and available for review for audits e.g. for comments made on the PCS should be available.

8.3 	Endotoxin results are reviewed against the limits in Table 3.

- Excursions from the limit should be notified to QA and the user group representative.

# Trending and Periodic Reporting of Water Quality Results

9.1	Following receipt of the vendor water quality results the data is reviewed against the previous weeks results to check for repeat limit excursions.

9.2	Annually the data are trended in a report to confirm satisfactory performance of the generation skid.

9.3	The author of the annual trend report will send the report for review and approval to a Pilot Plant group representative and QA.

9.4   	The approved annual trend report will be stored in the document management system.

# Responsibilities

Asymchem Operators

- Trained as purified water samplers - responsible for the routine sampling of the PW System in the Pilot Plant as described in this procedure.

Operations and Facility Lead or delegate

- Review of contractor test results final report,

- Assessment of contractor deviations for potential to impact Asymchem generated results,

- Impact assessments for results exceeding alert limit with QA,

- Raise deviations for purified water results exceeding action limits,

- Request additional sampling as necessary following intrusive works in discussion with QA.

- Annual trend report.

Quality Assurance

- Impact assessments for results exceeding alert or action limit

- Assess and review deviations for purified water results exceeding action limits

- Collaborates with Operations and Facility Lead in cases where additional samples may be required (see SOP-BLD-030 Engineering Works on Asymchem Sandwich Pilot Plant Purified Water System.)

- Review and approval of the annual trending report.

# References

| QF13070 | B902 Purified Water Sampling Point Rota Microbial, Chemical and Endotoxin Analysis |
| --- | --- |

# Revision History

| Summary of Changes | Justification of Change |
| --- | --- |
| - Addition of scheduling form QF13070 B902 Purified Water Sampling Point Rota to incorporate user points. | - Operational improvement. |